## surface collector
Sizing of ground source heatpumps WPSW
SURFACE COLLECTOR
choice of temperatures
choice of heat pump size
real heating output
|  |  | 19.5 | kW
choice of type of soil:
| usable heat quantity |  |  | surface required
| minimal | maximal |  | from | to
| 30 | 35 | W/m² | 557.1429 | 650 | m²
tube length
| collector | 500 | m
tube length
| feed pipe | 20 | m
| dimension collector |  | HDPE-tube 20 x 1,9 |  | HDPE-tube 25 x 2,3
| dimension feed pipe |  | HDPE-tube 28 x 1,5 |  | HDPE-tube 28 x 1,5
| anti freeze temp. |  | number of canisters with 20 ltrs. content ( round up!!)
| -10 °C |  | 1.125 |  | 1.725
| -20 °C |  | 1.85 |  | 2.85
| -30 °C |  | 2.3825 |  | 3.725
Remark: All grey arrays are results of calculations and must not be changed !!
c) 2009
dry sandy soil
moist sandy soil
dry loamy soil
moist loamy soil
aquiferous soil

## ground probe
Sizing of ground source heatpumps WPSW
GROUND PROBE
choice of temperatures
choice of heat pump size
real heating output
|  |  | 19.5 | kW
| usable heat quantity |  |  | needed total probe length
| normal | max. |  | from | to
| 50 | 60 | W/m | 325 | 390 | m
OERTLI recommend from technical and allowance reasons to limit
the depth at 99 meters for the probe.
If possible you should aspire a depth of 70 meters !!
There are always 4 tubes in each probe.
tube length
| feed pipe | 20 | m
| dimension probe |  | Ø 25,3 mm |  | Ø 32,0 mm
| dimension feed pipe |  | HDPE-tube 28 x 1,5 |  | HDPE-tube 35 x 1,5
| anti freeze temp. |  | number of canisters with 20 ltrs. content ( round up!!)
|  |  | min | max | min | max
| -10 °C |  | 4.325 | 5.17 | 6.985 | 8.35
| -20 °C |  | 7.25 | 8.68 | 11.86 | 14.2
| -30 °C |  | 9.525 | 11.41 | 15.435 | 18.49
Remark: All grey arrays are results of calculations and must not be changed !!
c) 2009

## Zahlen (hidden)
dry sandy soil | 10 | 15 | W/m²
moist sandy soil | 15 | 20 | W/m²
dry loamy soil | 20 | 25 | W/m²
moist loamy soil | 25 | 30 | W/m²
aquiferous soil | 30 | 35 | W/m²
| 5 | 30 | 35
refrigerant 0°C / Water 35°C
refrigerant 5°C / Water 35°C
refrigerant 0°C / Water 50°C
|  | S0W35 | S5W35 | S0W50
WPSW 8 |  | 7.5 | 8.9 | 6.6 | 0
WPSW10 |  | 9.7 | 11.3 | 8.9 | 0
WPSW 13 |  | 13.4 | 15.9 | 12.4 | 0
WPSW 16 |  | 16.2 | 19.5 | 15.4 | 19.5
19.5
Temperaturdouble | 2
ausgewählte WP | 4 | 8 | 16
Prinzip der Matrix
1 | 5 | 5 | 10 | 15
2 | 6 | 6 | 12 | 18
3 | 7 | 7 | 14 | 21
| 8 | 8 | 16 | 24
Tempdoubles 1-3
Wärmepumpe 1-4 = 5-8, um multiplizieren zu können
1=5; 2=6; 3=7; 4=8
berechnete Matrix aus Tempdoubles x Wärmepumpe
Ergebnis aus Matrix
logische Abfrage mit Matrix